# National Park Service (NPS) Regional Haze SIP technical feedback for the Nevada Division of Environmental Protection

July 25, 2022

Contents

1	Executive Summary	2

2	Updated Review: Nevada Energy – North Valmy Generating Station	2

2.1	Plant Characteristics	2

2.2	Recent Emissions	3

2.3	Evaluation of the Clean Air Act Statutory Factors at North Valmy	3

2.4	SO2 – Cost of Compliance	3

2.5	NOx – Cost of Compliance	8

2.6	Conclusions & Recommendations	8

# Executive Summary

The NPS appreciates the updated analyses provided by the Nevada Division of Environmental Protection (NDEP) and Nevada Energy in response to NPS consultation comments as part of the public review State Implementation Plan (SIP).  In the current draft SIP, NDEP provides supplementary information regarding Nevada Energy’s North Valmy Generating Station.  Based on this new information The NPS supports NDEP’s determinations that:

- Additional nitrogen oxide (NOx) and sulfur dioxide (SO2) emission controls are not reasonable for North Valmy Unit 2.

- Additional NOx emission controls are not reasonable for North Valmy Unit 1.

Nonetheless, the NPS’s updated review finds that Dry Sorbent Injection (DSI) continues to provide technically feasible and cost-effective opportunities to reduce SO2 emissions from North Valmy Unit 1 in this planning period.  NPS analyses discussed below and documented in the attached calculation workbooks demonstrate that adding DSI to North Valmy Unit 1 is within the cost-effectiveness threshold established by Nevada for this round of regional haze planning.

Replacement of the existing hydrated lime DSI system by a new one with greater capacity could reduce SO2 emissions by an additional 500 tons/year and result in an incremental cost-effectiveness of about $9,100/ton.

Replacement of the existing hydrated lime DSI system with DSI using milled trona could reduce SO2 emissions by 1,200 tons/year for about $9,500/ton.  This estimate includes the additional cost of adding powdered activated carbon (PAC) to address a potential brown plume.

The NPS recommends that Nevada require the most effective control measures found to be technically feasible and cost effective through analysis of the four factors specified in the Regional Haze Rule.  Those control measures include DSI for Unit 1 at North Valmy.

# Updated Review: Nevada Energy – North Valmy Generating Station

## Plant Characteristics

The North Valmy Generating Station (North Valmy) is a 522-megawatt (MW) coal-fired power station located near Valmy, Nevada.  This facility is about 300 km northwest of Great Basin National Park.  Additionally, the facility is 500km northwest of Zion National Park and 400km southwest of Craters of the Moon National Monument, both NPS-managed and federally-mandated Class I areas.  The plant is now owned by NV Energy.  Bituminous and subbituminous coal from mines in CO, UT, and WY is burned in two wall-fired boilers.  Sierra Pacific Resources began construction on the plant in 1979.

Unit 1 went online in 1981 and is rated at 254 MW with a Babcock & Wilcox (B&W) Boiler and Westinghouse turbine/generator.  Unit 1 is equipped with Low-NOx Burner (LNB) Technology to control nitrogen oxides (NOx) and a baghouse to control particulate.  Unit 1 utilizes a Dry Sorbent Injection (DSI) system employing hydrated lime on Unit 1.  The existing DSI system on Unit 1 is used to ensure compliance with the Mercury and Air Toxics Standards (MATS) hydrochloric acid (HCl) emission limit, and hydrated lime was selected as the appropriate sorbent to use on Unit 1 because of its capability to selectively react with HCl.  Unit 1 has no dedicated sulfur dioxide (SO2) controls.

Unit 2 followed in 1985 and is rated at 268 MW with a Foster Wheeler Boiler and General Electric turbine/generator.  Unit 2 is equipped with LNB, Dry Lime Flue Gas Desulfurization (FGD), and a baghouse.

## Recent Emissions

The table below provides a breakdown by unit of 2021 SO2 and NOx emissions and how they rank versus the 3,291 EGUs in EPA’s Clean Air Markets Database (CAMD).

Table 1.  2021 North Valmy EGU emissions and rank compared to other U.S.  EGUs in CAMD

| Unit ID | Operating Time | Gross Load (MW-h) | SO2 (tons) | SO2 Rank | Calculated Avg. SO2 Rate (lb/MMBtu) | Calculated Avg. NOx Rate (lb/MMBtu) | NOx (tons) | NOx Rank | CO2 (short tons) | CO2 Rank | Heat Input (MMBtu) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 4,797 | 621,369 | 1,646 | 152 | 0.577 | 0.329 | 938 | 254 | 598,297 | 867 | 5,704,571 |
| 2 | 6,668 | 1,177,825 | 747 | 279 | 0.131 | 0.256 | 1,455 | 147 | 1,193,194 | 348 | 11,376,761 |

## Evaluation of the Clean Air Act Statutory Factors at North Valmy

### Remaining Useful Life

Nevada Energy has committed to cease operations and shutdown both electrical generating units (EGUs) at North Valmy by December 31, 2028.  For this reason, the remaining useful life of these emission units becomes a critical statutory factor that also drives the cost of compliance statutory factor.  With this in mind, the NPS evaluated addition of Dry Sorbent Injection (DSI), scrubber upgrades, and Selective Non-Catalytic reduction (SNCR), which have relatively low capital costs and can be installed in a relatively short time.  As a result, we can assume a remaining useful life of four years for these control technologies, which is consistent with NDEP.

### Time Necessary for Compliance

Because of the relatively short remaining useful life of this facility, NPS review is limited to control strategies that can be implemented relatively quickly.  The NPS review of similar coal-fired EGUs indicates that DSI, scrubber upgrades, and SNCR can be installed in less than two years.

### Energy and Non-air Quality Impacts

The NPS agrees with NDEP that while energy and non-air quality impacts are considered as separate factors, they typically contribute to adjustments to the cost of compliance.  Furthermore, no unique or unusual energy and non-air quality impacts have been raised by Nevada Energy for North Valmy.

## SO2 – Cost of Compliance

### Unit 1 – Dry Sorbent Injection (DSI)

NDEP bases its analysis of DSI in the draft SIP on information provided by Nevada Energy (NVE).  The NPS was unable to review the full analysis completed by Sargent & Lundy (S&L) in 2012 on behalf of NVE due to its redaction from the SIP documentation.  Nonetheless, in its April 29, 2022 submittal, NVE states that it will accept the use of information over ten years from the redacted S&L study because the Environmental Protection Agency (EPA) has relied upon information that is more than ten years old in some instances.

Alternatively, recent revisions to the EPA Control Cost Manual (CCM) are based upon algorithms developed by S&L for SNCR (2017), SCR (2017), and SDA/CDS (2017), and Wet FGD (2017).  For example, Sargent & Lundy published “Dry Sorbent Injection for SO2 Control Cost Development Methodology” in March 2013 and updated it in 2017 to include some significant changes for EPA’s Integrated Planning Model (IPM). Instead of relying upon that 2013 model, NPS analyses use the current (2017) model.

NVE states:

Moreover, two of the cost elements of the S&L estimate that NPS describes as being inappropriate (owner’s costs and allowance for funds used during construction) are specifically included in the IPM model that NPS itself used to develop its own DSI cost estimates as documented in the worksheet provided.

The EPA has consistently rejected the inclusion of owner’s costs ($4,880,900 for DSI with trona according to NVE) and allowance for funds used during construction.  The NPS used the IPM which allows the exclusion of these costs.  Consistent with EPA recommendations, NPS analyses excluded these costs.

NVE states:

Moreover, NPS cost analysis presents a capital recovery cost for this alternative that appears to be based on a cost of capital of 4.72%.  In our previously submitted response letter dated July 8, 2020, we explained why the cost of capital for NVE’s operating utilities that is set by the Public Utility Commission of Nevada (6.75%) is the preferred firm-specific cost of capital for us to use when evaluating the economics of emissions control options.  Consequently, NVE believes that NPS estimates of both the capital cost of a trona-based DSI system for North Valmy as well as the annualized cost of that capital are understated.

All NPS cost calculations for NVE sources consistently applied NVE’s 6.75% interest rate.

#### New DSI with hydrated lime

The NPS encourages evaluating the replacement of the existing hydrated lime DSI with a hydrated lime system with higher capacity.  While DSI with hydrated lime and a baghouse can achieve a maximum of 70% removal (S&L IPM model), this would suffice to eliminate the need to address a brown plume associated with the DSI with Milled Trona option.

NVE states in their April 29, 2022 letter:

In Table 2 of Section 4.1.4 of their comments summary document, NPS presents an estimate of the capital and annual operating costs associated with replacing the existing hydrated lime- based DSI system on North Valmy Unit 1, and asserts that replacing the existing hydrated lime- based DSI system with a new system would be cost effective.  NVE finds this comment to be confusing because Unit 1 is already equipped with a hydrated lime based DSI system.  That system was installed less than seven years ago, and there is no technical or economic reason to replace this existing system.  Moreover, NPS cost estimate assumes that a hydrated lime- based DSI system would achieve 50% removal of SO2.  Based on our existing system’s performance, however, this technology achieves a much lower level of SO2 control (22%) as noted above.

NVE states in their May 27, 2022 letter:

From a theoretical perspective, increasing the SO2 control efficiency of the existing DSI system on Unit 1 would require an increase in the rate at which hydrated lime is injected… a much greater quantity of sorbent than is currently used would need to be injected to control SO2 emissions from Unit 1 with the existing hydrated lime-based DSI system.  As an increased lime injection rate would cause plugging problems and potentially make the collected fly ash hazardous, NVE does not consider this to be a technically feasible alternative.

The NPS recognizes that the existing hydrated lime DSI system does not have the capacity to inject sorbent at the rate necessary to achieve the 50% control level consistent with this technology and suggests investigating replacement of the existing hydrated lime DSI system with one of greater capacity.  NVE also raises the possibility that increased lime in the solid waste stream could render this material hazardous.  The NPS has not encountered this concern with other, similar systems.

#### DSI with milled trona:

NPS review finds that the updated NVE analysis overestimates the costs of control for DSI with milled trona in the following circumstances.

- NVE assumed that DSI with milled trona and a baghouse could achieve only 73.8% SO2 removal.  In contrast, S&L’s IPM model assumes 90% control.

- NVE’s Contingency Cost is 17% of the sum of the Direct Costs and Indirect Costs; the CCM recommends that “A default value of 10% of the direct and indirect costs is typically used for CF [Contingency Factor].  However, values of between 5% and 15% may be used.”

- NVE included a $4.9 million Owner’s Cost which is not allowed by the CCM.

- NVE did not account for the cost savings resulting from elimination of the existing DSI system.

Further, Direct Costs and Indirect Costs in the NVE analysis of this control option could not be confirmed.  Supporting documentation for Direct Costs and Indirect Costs would improve the justification for the resulting calculations.

#### Updated NPS Analyses

The NPS agrees with NDEP that 2019 was not representative of current plant operations, as a result 2016–2018 and 2020–2021 data from CAMD are used.  The NPS developed estimates based upon the S&L DSI IPM model.

The NPS applied the S&L DSI IPM methodologies for DSI with hydrated lime and with milled trona.  Analyses assumed that the existing hydrated lime system is completely depreciated, so the capital recovery costs of any new systems would be new (as well as the associated fixed maintenance cost assumed = 1.5% of the Total Capital Investment per the CCM).  The NPS also assumed that the existing hydrated lime injection system would be replaced and deducted those operating costs from the analysis.  The NPS added NVE’s estimate for addition of PAC to the Milled Trona option and based uncontrolled SO2 emissions on the NVE estimates of 22% control efficiency by the existing DSI and 1,812 tons of annual emissions.

Table 2.  NPS DSI Control Cost Estimates for North Valmy Unit 1

| Sorbent | Existing Hydrated Lime | New Hydrated Lime | New Hydrated Lime Incrementals | Milled Trona | Milled Trona Incrementals | Units |
| --- | --- | --- | --- | --- | --- | --- |
| Total Capital Investment |  | $ 14,063,839 | $ 14,063,839 | $ 24,304,927 | $ 24,304,927 | (2019$) |
| Capital Recovery Cost |  | $ 4,128,632 | $ 4,128,632 | $ 7,135,044 | $ 7,135,044 | /yr |
| Fixed O&M |  | $ 339,850 | $ 339,850 | $ 400,135 | $ 364,574 | /yr |
| PAC Cost |  |  |  | $ 1,910,600 | $ 1,910,600 | /yr |
| Variable O&M Cost | $ 1,056,810 | $ 1,192,260 | $ 135,451 | $ 3,336,615 | $ 2,279,806 | /yr |
| Total Annual Cost | $ 5,232,047 | $ 5,660,743 | $ 4,603,933 | $ 12,782,394 | $ 11,690,023 | /yr |
| Uncontrolled SO2 | 1,812 | 1,812 |  | 1,812 |  | ton/yr |
| SO2 Removed | 399 | 906 | 507 | 1,631 | 1,232 | ton/yr |
| Cost-Effectiveness | $ 13,125 | $ 6,248 | $ 9,074 | $ 7,838 | $ 9,487 | $/ton |

Even though the use of hydrated lime does not remove SO2 as effectively as milled trona, its capital costs and operating expenses are much lower, resulting in an incremental cost-effectiveness of about $9,100/ton to replace the existing hydrated lime system with a new one of greater capacity.  With the additional cost of adding PAC, the incremental cost-effectiveness of replacing the existing hydrated lime DSI system with DSI using milled trona is still approximately $9,500/ton.

### Unit2 – Dry Lime FGD System Upgrades

Based on Energy Information Administration fuels data for North Valmy for 2020, the scrubber on Unit 2 is achieving 78% efficiency.  Modern FGD systems regularly achieve greater than 95% control.  Scrubber upgrades to improve efficiency are often very cost effective.  The NPS appreciates that the NDEP requested and NVE provided a full four-factor analysis which includes this response:

NPS states in Section 4.1.4 of the comments summary document that modern FGD systems “regularly” achieve better than 95% control of SO2.  NVE agrees that this statement may be true for certain types of new FGD systems, but disagrees with the assertion that upgrading the existing FGD system on North Valmy Unit 2 would be cost effective.  As we explained in our letter dated January 15, 2021, the performance of the existing FGD system on Unit 2 has already been fully optimized; the system was designed to achieve 70% SO2 removal but now achieves at least 78% removal.  As explained below, further improvement of the performance of this system would require that the existing multi-nozzle spray dryer vessels would need to be reconfigured to single nozzle spray dryer vessels in order to achieve any additional improvement in the control of SO2.  As shown below, this alternative would not be cost effective considering the commitment to retire this unit at the end of 2028.

#### Identification of control options

The existing lime spray dryer based FGD system on North Valmy Unit 2 consists of three spray dryer absorber vessels operating in parallel.  Each vessel is equipped with three separate lime slurry atomizers that spray reagent near the top of the vessel in an overlapping pattern that contacts the flue gas from the unit in a counter-current fashion.  As noted in the NPS submittal dated January 15, 2021, this existing system has already been optimized to the extent possible by using the highest quality lime commercially available, by using recycled system ash as well as fresh lime to increase the available reagent surface area, by operating at the lowest feasible saturation approach temperature, and by optimizing the spray coverage available with the multi-nozzle configuration.  The only technically feasible alternative to further improve the SO2 control efficiency of this system would entail replacement of the existing multi-nozzle atomizer system in each vessel with a single nozzle design that would provide nearly 100% spray coverage across the flue gas flow pattern.

#### Cost of controls

A detailed engineering study of the technical and economic feasibility of retrofitting the existing multi-nozzle atomizer-based FGD system on Unit 2 with a single nozzle- based system has not been conducted.  In 2013, NVE received budgetary cost information for the principal equipment that would be required to implement this alternative from the vendor of this equipment, Babcock & Wilcox (B&W).

As shown in the attached cost estimate, the estimated capital cost of retrofitting the existing multi- atomizer spray dryers with single atomizer systems is over $46 million.  The total annualized cost of this alternative, assuming that it would be operational by the end of 2024, is estimated at over $17 million per year.  At an estimated SO2 control efficiency of 94%, this alternative would control a total 2,141 tons/yr based on the projected output of Unit 2 in 2028.  Thus, the overall cost effectiveness of this alternative is about $8,000 per ton controlled.  Compared to the current FGD system on Unit 2, this alternative would control an additional 364.4 tons/yr; in this regard, the system retrofit would have an incremental cost effectiveness of over $46,500 per additional ton removed.

Because the CCM advises against escalating costs more than five years to account for inflation, The NPS used the 2013 budgetary Basic Equipment Cost estimated provided by Babcock & Wilcox to NVE of $11,400,000 to estimate the Total Capital Investment.  The NPS notes that the costing method used by NVE is inconsistent with the CCM method described below.  For example, NVE’s method assumed that the Direct Installation Cost is 90% of the Purchased Equipment Cost (PEC) versus the CCM estimate = 85% of the PEC.  NVE also estimated the Indirect Costs at 45% of the PEC versus the CCM estimate = 32%. (NVE included 977,000 in Owner’s Costs which are not allowed by the CCM.) The NPS used the method shown in Table 1.8: Capital Cost Factors for Wet Packed Tower Absorbers in 7th edition of the CCM, Section 5 (SO₂ and Acid Gas Controls), Chapter 1 (Wet and Dry Scrubbers for Acid Gas Control) to estimate the Total Capital Investment (TCI) to upgrade the Unit 2 scrubber would be $27,211,800, which leads to an annual capital cost of $7,989,384.

To estimate the increase in Direct Annual Costs due to increased consumables, the NPS applied the CCM workbook for Spray Dry Absorbers to both the existing control scenario and to a 94% control scenario.  The NPS estimates the costs of increased scrubbing to exceed $112,000/yr.  Total Annual Cost of the scrubber upgrade would be about $16.5 million and remove an additional 395 tons of SO2 per year.  The cost-effectiveness of the upgrade ($21,534/ton) would more than double the NDEP threshold, making further analysis unnecessary.

## NOx – Cost of Compliance

The NPS applied the 2021 version of EPA’s CCM for SNCR (with the 2021 Chemical Engineering Plant Cost Index = 776.3) and the results are shown below.  Due to the assumption of a four-year remaining useful life, capital recovery costs dominate the analyses.  The cost-effectiveness for SNCR at North Valmy is outside the threshold set by NDEP for this round of regional haze planning.

Table 3.  SNCR Control Cost Estimates for North Valmy Units 1 & 2

| Unit | N Valmy 1 | N Valmy 2 |  |
| --- | --- | --- | --- |
| Total Capital Investment | $11,677,729 | $11,998,813 | (2021$) |
| Capital Recovery Cost | $3,428,581 | $3,522,852 | /yr |
| Direct Annual Cost | $694,059 | $971,255 | /yr |
| Total Annual Cost | $4,127,895 | $4,499,506 | /yr |
| Uncontrolled NOx | 772 | 1,147 | ton/yr |
| NOx Removed | 184 | 263 | ton/yr |
| Cost-Effectiveness | $22,485 | $17,110 | $/ton |

## Conclusions & Recommendations

### Cost of Compliance

Adding DSI to North Valmy Unit 1 to reduce SO2 emissions is within the cost-effectiveness threshold established by Nevada for this round of regional haze planning.

  - Replacement of the existing hydrated lime DSI system with a new one with greater capacity with hydrated lime could reduce SO2 by an additional 500 tons/year, resulting in an incremental cost-effectiveness of about $9,100/ton.

  - With the additional cost of adding PAC, the incremental cost-effectiveness of replacing the existing hydrated lime DSI system with DSI using milled trona is still about $9,500/ton and would remove an additional 1,200 tons/year.

North Valmy Unit 2 is achieving about 80% SO2 control efficiency.  Modern FGD systems regularly achieve better than 95% control.  NDEP required that NVE conduct a four-factor analyses focused on upgrading the FGD on Unit 2.  NPS review of the NVE analysis confirms that a scrubber upgrade would exceed the NDEP cost-effectiveness by more than a factor of two.

Analysis of SNCR’s potential to reduce NOx emissions at North Valmy Units 1 & 2 is not within the cost-effectiveness threshold set by Nevada and exceeds the thresholds used by other states for this regional haze planning period.

### Other Factors

NVE has not shown that Energy and Non-Air Environmental Impacts raised as concerns for DSI are unique to this situation.

Time Necessary for Compliance is expected to be less than two years.

Remaining Useful Life will be limited by federally enforceable conditions.

### Conclusion

The NPS requests that Nevada require the most effective control measures found to be technically-feasible and cost-effective through analysis of the four factors specified in the Regional Haze Rule.  Those control measures include DSI for Unit 1 at North Valmy.

Dry Sorbent Injection for SO2/HCl Control Cost Development Methodology (epa.gov)

EPA used the S&L IPM methodologies as the basis for its recent CCM updates for SNCR, SCR, and SDA/CDS/Wet FGD.