## N Valmy 1980-2021 unit annual
State | Facility Name | Facility ID (ORISPL) | Unit ID | Year | Operating Time | # of Months Reported | Gross Load (MW-h) | Gross Load (MW) | SO2 (tons) | Calculated Avg. SO2 Rate (lb/MMBtu) | Avg. NOx Rate (lb/MMBtu) | Calculated Avg. NOx Rate (lb/MMBtu) | NOx (tons) | CO2 (short tons) | Unit 1 Heat Input (MMBtu) | Heat Rate (MMBtu/MWh) | County | Unit Type | Fuel Type (Primary) | Fuel Type (Secondary) | SO2 Control(s) | NOx Control(s) | PM Control(s) | Hg Control(s) | Facility Latitude | Facility Longitude
NV | North Valmy | 8224 | 1 | 1980 |  | 0 |  | #DIV/0! | 0 | #DIV/0! |  | #DIV/0! |  |  | 0 | #DIV/0! | Humboldt County | [7 empty] | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 1985 |  | 0 |  | #DIV/0! | 7998 | 0.78841 |  | 0 |  |  | 20289036 | #DIV/0! | Humboldt County | Dry bottom wall-fired boiler |  |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 1990 |  | 0 |  | #DIV/0! | 5203 | 0.6523 |  | 0 |  |  | 15952867 | #DIV/0! | Humboldt County | Dry bottom wall-fired boiler |  |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 1995 |  | 0 |  | #DIV/0! | 3075 | 0.6027 |  | 0.26813 | 1368 | 1046790 | 10204109 | #DIV/0! | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 1996 |  | 0 |  | #DIV/0! | 4685.9 | 0.68553 |  | 0.32595 | 2228 | 1402757 | 13670923 | #DIV/0! | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 1997 | 8050.75 | 12 | 1589696.75 | 197.4595 | 4484.47 | 0.59732 | 0.303 | 0.3197 | 2400.186 | 1540578.55 | 15015396.85 | 9.4454 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 1998 | 8129.5 | 12 | 1924690.5 | 236.7539 | 5197.05 | 0.60156 | 0.387 | 0.40134 | 3467.239 | 1772776.225 | 17278498.7 | 8.9773 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 1999 | 8039 | 12 | 1947366.25 | 242.2399 | 5553.664 | 0.65663 | 0.3607 | 0.36997 | 3129.156 | 1772096.275 | 16915540.475 | 8.6864 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2000 | 8128 | 12 | 2111863.25 | 259.8257 | 5673.109 | 0.65747 | 0.3512 | 0.35309 | 3046.659 | 1790434.35 | 17257366.65 | 8.1716 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2001 | 6843.25 | 12 | 1701468 | 248.6345 | 4918.657 | 0.669 | 0.3393 | 0.34369 | 2526.899 | 1508683.35 | 14704512.5 | 8.6423 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2002 | 8226.5 | 12 | 2007543 | 244.0337 | 5321.934 | 0.54734 | 0.2926 | 0.29385 | 2857.165 | 1995231.375 | 19446704.6 | 9.6868 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2003 | 8183.75 | 12 | 2007463 | 245.2987 | 6021.105 | 0.60498 | 0.332 | 0.33431 | 3327.226 | 2042259.15 | 19905097.075 | 9.9155 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2004 | 8159.75 | 12 | 1970571.5 | 241.499 | 7195.78 | 0.7325 | 0.3587 | 0.36015 | 3537.976 | 2015794.925 | 19647133.175 | 9.9703 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2005 | 7726.5 | 12 | 1878619.5 | 243.1398 | 7395.987 | 0.77895 | 0.3963 | 0.40003 | 3798.216 | 1948343.85 | 18989675.05 | 10.1083 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2006 | 6777 | 12 | 1593543.75 | 235.14 | 5352.33 | 0.69406 | 0.3455 | 0.35055 | 2703.301 | 1582433.225 | 15423315.5 | 9.6786 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2007 | 7926.38 | 12 | 1854536.24 | 233.9701 | 5988.691 | 0.68061 | 0.3366 | 0.33981 | 2989.967 | 1805565.366 | 17598085.222 | 9.4892 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2008 | 7642.68 | 12 | 1760245.32 | 230.3178 | 6687.59 | 0.85044 | 0.333 | 0.33774 | 2655.86 | 1638712.19 | 15727430.428 | 8.9348 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2009 | 7397.13 | 12 | 1611220.21 | 217.8169 | 4923.383 | 0.68797 | 0.2711 | 0.27353 | 1957.467 | 1501118.946 | 14312758.298 | 8.8832 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2010 | 8253.52 | 12 | 1686810.76 | 204.3747 | 5154.017 | 0.68709 | 0.3434 | 0.34238 | 2568.271 | 1573458.725 | 15002408.91 | 8.8939 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2011 | 5213.5 | 12 | 872484.29 | 167.351 | 2513.106 | 0.64879 | 0.3192 | 0.32962 | 1276.783 | 812506.338 | 7747031.342 | 8.8793 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2012 | 5754.1 | 12 | 928134.58 | 161.2997 | 2893.482 | 0.7198 | 0.2877 | 0.29385 | 1181.238 | 843206.536 | 8039726.674 | 8.6622 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2013 | 7531.88 | 12 | 1348975.88 | 179.1021 | 5123.241 | 0.82605 | 0.2618 | 0.26917 | 1669.426 | 1300941.872 | 12404117.933 | 9.1952 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2014 | 7739.59 | 12 | 1662292.51 | 214.7779 | 6363.464 | 0.83415 | 0.2878 | 0.29409 | 2243.468 | 1600172.669 | 15257271.807 | 9.1785 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2015 | 7662.21 | 12 | 1256559.67 | 163.9944 | 4469.762 | 0.77362 | 0.2932 | 0.29222 | 1688.366 | 1211930.025 | 11555381.734 | 9.196 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2016 | 3433.09 | 12 | 557936.6 | 162.5173 | 1847.863 | 0.75545 | 0.3205 | 0.32583 | 797.001 | 513083.711 | 4892103.712 | 8.7682 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2017 | 2326.96 | 12 | 353877.45 | 152.0772 | 1232.41 | 0.75744 | 0.3654 | 0.3609 | 587.204 | 341292.091 | 3254124.459 | 9.1956 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2018 | 3870.4 | 12 | 677681.35 | 175.0934 | 2356.752 | 0.76394 | 0.3265 | 0.33279 | 1026.665 | 647106.181 | 6169957.33 | 9.1045 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2020 | 3698.34 | 12 | 442284.27 | 119.5899 | 1458.399 | 0.68937 | 0.319 | 0.32101 | 679.102 | 443757.067 | 4231094.178 | 9.5665 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
NV | North Valmy | 8224 | 1 | 2021 | 4796.63 | 12 | 621368.89 | 129.5428 | 1645.753 | 0.57699 | 0.3248 | 0.32894 | 938.228 | 598296.644 | 5704571.116 | 9.1807 | Humboldt County | Dry bottom wall-fired boiler | Coal |  |  | Low NOx Burner Technology (Dry Bottom only) | Baghouse |  | 40.8831 | -117.1542
|  |  |  | Totals | 14692.33 |  | 2095211.96 |  | 6693.314 |  |  |  | 3231.199 |  | 19359747.083
|  |  |  | Averages | 3673.0825 |  | 523802.99 | 144.0758 | 1673.3285 | 0.69147 |  | 0.096926 |  |  | 4839936.7708 | 9.24
[10 empty] | 22% | control efficiency
[10 empty] | 0.8865 | uncontrolled

## Capital Costs
DSI Capital Cost Estimate Worksheet
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 254 | company 4-factor report
Retrofit Factor | B |  | 1 | NPS assumption
Gross Heat Rate | C | (Btu/kWh) | 9239.9945 | CAMD
SO2 Rate | D | (lb/MMBtu) | 0.8865 | from CAMD and NVE @ 22% control | Bituminous | ESP | TRUE
NSR | K |  | 2.6085 | Unmilled Trona with an ESP = If(H<40.0,0.0350*H,0.352e(0.0345*H)) Milled Trona with an ESP = If(H<40.0,0.0270*H,0.353e(0.0280*H)) Unmilled Trona with an BGH = If(H<40.0,0.0215*H,0.295e(0.0267*H)) Milled Trona with an BGH = IF(H<40.0,0.0160*H,0.208e(0.0281*H))
Trona Feed Rate | M | (ton/hr) | 6.5186 | (1.2011*10-6)*K*A*C*D
CEPCI (2016) |  |  | 541.7 | NPS from OAQPS
CEPCI (2021$) |  |  | 776.2 | NPS from OAQPS
Costs are all based on 2016 dollars
Capital Cost Calculation
Include: equipment, installation, buildings, foundations, electrical, and retrofit difficulty.
BM ($) = Unmilled Trona, If(M>25 then (745,000*B*M) else (7,500,000*B*M0.284) Milled Trona, If(M>25 then (750,000*B*M) else (7,516,000*B*M0.284) |  |  | 14135080.3074 | Base module absorber island cost
BM ($/kW) |  |  | 55.6499 | Base module cost per kW
Total Project Cost
A1 = 10% of BM |  |  | 1413508.0307 | Engineering and construction management costs
A2 = 5% of BM |  |  | 706754.0154 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc..
A3 = 5% of BM |  |  | 706754.0154 | Contractor profit and fees
CECC($) - excludes owner's costs = BM+A1+A2+A3 |  |  | 16962096.3689 | Capital, engineering and construction cost subtotal
CECC($/kW) - excludes owner's costs = |  |  | 66.7799 | Capital, engineering and construction cost subtotal per kW
Total Capital Investment = |  |  | 24304927.4535 | (2019$)

## O&M Costs
DSI Capital Cost Estimate Worksheet
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 254 | company 4-factor report |  | `
Retrofit Factor | B |  | 1 | NPS assumption
Gross Heat Rate | C | (Btu/kWh) | 9239.9945 | CAMD
SO2 Rate | D | (lb/MMBtu) | 0.8865 | from CAMD and NVE @ 22% control
Type of Coal | E | Bituminous |  | company 4-factor report |  |  | PRB | BGH | FALSE
Particulate Capture | F | BGH |  | company 4-factor report |  |  | Lignite
Milled Trona | G | TRUE |  | IPM example
Removal Target | H |  | 90 | Maximum Removal Targets: Unmilled Trona with an ESP = 65% Milled Trona with an ESP = 80% Unmilled Trona with a BGH = 80% Milled Trona with a BGH = 90%
Heat Input | J | (Btu/hr) | 2346958614.6702 | A*C*1000
NSR | K |  | 2.6085 | Unmilled Trona with an ESP = If(H<40.0,0.0350*H,0.352e(0.0345*H)) Milled Trona with an ESP = If(H<40.0,0.0270*H,0.353e(0.0280*H)) Unmilled Trona with an BGH = If(H<40.0,0.0215*H,0.295e(0.0267*H)) Milled Trona with an BGH = IF(H<40.0,0.0160*H,0.208e(0.0281*H))
Trona Feed Rate | M | (ton/hr) | 6.5186 | (1.2011*10-6)*K*A*C*D
Sorbent Waste Rate | N | (ton/hr) | 5.2314 | (0.7387+0.00185*H/K)*M; Based on a final reaction product of NA2SO4 and unreacted drysorbent as NA2CO3
Fly Ash Waste Rate | P | (ton/hr) | 10.2413 | (A*C)*Ash in Coal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.012; Boiler Ash Removal = 0.2; HHV= 11000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2; HHV= 8400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2 HHV= 7200
Aux Power | Q | (%) | 0.51328 | If Milled Trona M*20/A, else M*18/A
Trona Cost | R | ($/ton) | 167 | company 4-factor report
Waste Disposal Cost | S | ($/ton) | 30 | company 4-factor report
Aux Power Cost | T | ($/kWh) | 0.05 | company 4-factor report
Operating Labor Rate | U | ($/hr) | 60 | company 4-factor report
Interest Rate |  | (%) | 6.75 | NVDEP
Control Equipment Life |  | (yr) | 4 | NPS assumption
Capital Recovery Factor |  | CRF | 0.29356 | calculated
Effective annual operating hours, top |  | (hr/yr) | 3673.0825 | CAMD
Gross Load |  | (MW-h) | 523802.99 | CAMD
Costs are all based on 2016 dollars
Fixed O&M Cost
FOMO ($/kW yr) = (2 additional operator)*2080*U/(A*1000) |  |  | 0.98268 | Fixed O&M additional operating labor costs | 249600
FOMM ($/kW yr) = BM*0.01/(B*A*1000) |  |  | 0.5565 | Fixed O&M maintenance material and labor costs | 141350.8031
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  |  | 0.036158 | Fixed O&M additional addministrative labor costs | 9184.2096
400135.0127
FOM ($/kW yr) = FOMO + FOMM |  |  | 1.5753 | Total Fixed O&M costs | 400135.0127
Variable O&M
VOMR ($/MWh) = M*R/A |  |  | 4.2859 | Variable O&M costs for lime reagent | 2244948.1702
VOMW ($/MWh)= (N+P)*S/A |  |  | 1.8275 | Variable O&M costs for waste disposal | 957239.0357
VOMP ($/MWh) = Q*T*10 |  |  | 0.25664 | Variable O&M costs for additional auxillary power required including additional fan power | 134428.0341
3336615.2401
VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM |  |  | 6.37 | Total variable O&M costs | 3336615.2401
Note on D39: Aaron J. Worstell: Confirm formula

## cost-effectiveness
Dry Sorbent Injection w Baghouse Cost Estimate
Sorbent | Milled Trona
Total Capital Investment | 24304927.4535 | (2021$)
Capital Recovery Cost | 7135043.6918 | /yr
Fixed O&M | 400135.0127 | /yr
Variable O&M Cost | 3336615.2401 | /yr
Powdered Activated Carbon | 1910600 | /yr
Total Annual Cost | 12782393.9446 | /yr
Uncontrolled SO2 | 1812 | ton/yr
SO2 Removed | 1630.8 | ton/yr
Cost-Effectiveness | 7838.1125 | $/ton